VIPA GmbH 08.09.2000

# Slave info tool

To read out the diagnostic messages from Flash VIPA provides you with the „Slave Info Tool“:

picture 1

The IM253DP stores the last 100 diagnostic messages in a  ring buffer structure inside RAM. Before a reboot happens, that structure is saved to Flash.

Every power down or power fail is stored with a timestamp in the EEPROM. At the next boot up, this event is saved as a diagnostic message in Flash. That way a lifetime counter for the IM253DP is realized.

Some events are only registered inside RAM because they happen during runtime (enter state ready, enter state data exchange, configuration error, parameterization error). If you want to save those events to Flash you need to manually store them: For slaves with Display use menu item „Sto“. For slaves with address switch select address 00 for 5 seconds. Now you can power down the Slave. All diagnostics data is stored nonvolatile in Flash.

On your Disk you’ll find the following  readme.txt :

Slave Info Tool     SINFO.EXE              VIPA GmbH 2000

==============================

The Program runs under Microsoft Windows 95,98,2000 and NT.

1. Start SINFO.EXE

2. Slave: At a slave without Display: Select Address 00 with the Address

Switches. After 5 Seconds the internal slave information was

saved to Flash and you can enter the Slaves original Profibus

Address again.

At a slave with Display: Select menu item: 'Sto' and press

up and down button together for 3 seconds. After the internal slave

information was saved to Flash you will see 'rdy' on the Display.

3. Slave: power off

4. Connect the vipa download-wire with the Slave IM253DP as shown

in the following picture:

--------

.... |      |

-----  |.....

.| |   .|

.      . |

.      .  |

........   |

|      |   |

|      |   |

|      |   |

|      |   |

|      |  .

|      | .

|      |.

|......|

5. Slave: power on (-> only the PW LED should light up)

6. In SINFO.EXE select your serial interface (e.g. COM1)

7. Click button 'connect' (you should see <connected> and a green OK label)

8. Click button 'get info -> display' to read slave information data on the tools'

screen.

Click button 'get info -> file' and select path and file name where to save

slave information data.

9. Click button 'show diag list' to get a description of the slave information

data.

10. Click button 'STOP' to clear the display

11. Slave: power off

12. Unplug vipa download-wire

How to interprete the diagnostics:

The button  „show diag list“ gives you a list of all possible events of the slave info structure

Picture 2

Byte0  Message

================================================

0A:  DP Parameter Error

Byte1: 1..32=slot ; 0=unknown

Byte2: length of user parameters

Byte3: S7_400_Mode: 0=off 1=on

Byte4: number of digital modules (slave)

Byte5: number of analog  modules (slave)

Byte6: number of analog  modules (master)

14:  DP Configuration Length Error

Byte1: 1..32=slot ; 0=unknown

Byte2: number of config bytes (master)

Byte3: number of config bytes (slave)

Byte4: S7_400_Mode: 0=off 1=on

15:  DP Configuration Entry  Error

Byte1: 1..32=slot ; 0=unknown

Byte2: config byte (master)

Byte3: config byte (slave)

Byte4: S7_400_Mode: 0=off 1=on

1E:  Power fail or Power down

28:  VBUS Parameter Error

Byte1: 1..32=slot ; 0=unknown

29:  VBUS Initialization Error

2A:  VBUS Bus Error

2B:  VBUS QVZ

Byte1: 1..32=slot ; 0=unknown

32:  System 200V Diagnostic Alert

Byte1..Byte16: Alert data

33:  System 200V Process Alert

Byte1..Byte16: Alert data

3C:  New Slave Address set

3D:  Slave entered state READY

3E:  Slave entered state DATA_EXCHANGE

The diagnostics buffer starts with the number of the latest entry in the ringbuffer: diagcnt=XXXX.

Then up to 100 diagnostic messages follow. You can identify the message by it’s number:  n=XXXX:

Each message has a timestamp: d=XXXXh=XXm=XXs=XX

This means: day=...,  hour=....,  minute=....,  second=....

Then the user diagnostic part of the diagnosis follows:  diag=0x .. .. .. .. (23 bytes). On Profibus a diagnosis message contains 6 byte norm diagnostics first. Then the user diagnostic bytes follow. In the slave info structure only the user diagnosis part is stored.

diagcnt=0084

Power down or power fail

New slave address set

Slave entered state ready

DP Configuration Length Error

00 = unknown slot number

04 = number of config bytes (master)

03 = number of config bytes (slave)

00 = S7_400_Mode off

Therefore it‘s obvious what happened:

Module number 4 is faulty.

The master requests 4 modules but the slave only recognizes 3 modules on the vbus.

Slave entered state ready

Reboot due to VBUS bus error before!

VBUS bus error

(e. g. due to module dropout)

Slave entered state data exchange

no=0000: d=0000h=01m=31s=32 diag=0x1E 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00   no=0001: d=0000h=01m=31s=39 diag=0x1E 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00   no=0002: d=0000h=01m=32s=19 diag=0x1E 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00   no=0003: d=0000h=01m=42s=03 diag=0x1E 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00   no=0004: d=0000h=01m=42s=05 diag=0x3D 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00   no=0005: d=0000h=01m=42s=05 diag=0x3E 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00   no=0006: d=0000h=01m=42s=54 diag=0x3C 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00   no=0007: d=0000h=01m=42s=54 diag=0x1E 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00   no=0008: d=0000h=01m=42s=56 diag=0x3D 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00   no=0009: d=0000h=01m=43s=14 diag=0x3C 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00   no=0010: d=0000h=01m=43s=14 diag=0x1E 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00   no=0011: d=0000h=01m=43s=16 diag=0x3D 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00   no=0012: d=0000h=01m=43s=27 diag=0x3E 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00   no=0013: d=0000h=01m=45s=39 diag=0x3D 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00   no=0014: d=0000h=01m=45s=41 diag=0x3E 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00   no=0015: d=0000h=01m=46s=24 diag=0x1E 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00   no=0016: d=0000h=01m=46s=31 diag=0x1E 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00   no=0017: d=0000h=01m=46s=33 diag=0x3D 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00   no=0018: d=0000h=01m=46s=33 diag=0x3E 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00   no=0019: d=0000h=02m=57s=42 diag=0x3D 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00   no=0020: d=0000h=02m=58s=50 diag=0x3E 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00   no=0021: d=0000h=02m=58s=57 diag=0x3D 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00   no=0022: d=0000h=02m=58s=59 diag=0x3E 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00   no=0023: d=0000h=02m=59s=06 diag=0x3D 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00   no=0024: d=0000h=02m=59s=19 diag=0x3E 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00   no=0025: d=0000h=02m=59s=24 diag=0x3D 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00   no=0026: d=0000h=02m=59s=37 diag=0x3E 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00   no=0027: d=0000h=03m=00s=41 diag=0x3D 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00   no=0028: d=0000h=03m=03s=31 diag=0x3E 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00   no=0029: d=0000h=05m=13s=07 diag=0x3D 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00   no=0030: d=0000h=05m=13s=24 diag=0x2A 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00   no=0031: d=0000h=05m=13s=24 diag=0x1E 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00   no=0032: d=0000h=05m=13s=26 diag=0x3D 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00   no=0033: d=0000h=05m=14s=07 diag=0x2A 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00   no=0034: d=0000h=05m=14s=07 diag=0x1E 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00   no=0035: d=0000h=05m=14s=09 diag=0x3D 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00   no=0036: d=0000h=05m=18s=28 diag=0x3C 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00   no=0037: d=0000h=05m=18s=28 diag=0x1E 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00   no=0038: d=0000h=05m=18s=30 diag=0x3D 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00   no=0039: d=0000h=05m=18s=56 diag=0x3E 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00   no=0040: d=0000h=05m=18s=56 diag=0x3D 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00   no=0041: d=0000h=05m=18s=56 diag=0x3E 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00   no=0042: d=0000h=05m=20s=42 diag=0x2A 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00   no=0043: d=0000h=05m=20s=42 diag=0x1E 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00   no=0044: d=0000h=05m=20s=44 diag=0x3D 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00   no=0045: d=0000h=05m=20s=44 diag=0x14 00 04 03 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00   no=0046: d=0000h=05m=22s=43 diag=0x2A 00 04 03 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00   no=0047: d=0000h=05m=22s=43 diag=0x1E 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00   no=0048: d=0000h=05m=22s=54 diag=0x1E 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00   no=0049: d=0000h=05m=22s=56 diag=0x3D 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00   no=0050: d=0000h=05m=22s=56 diag=0x3E 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00   no=0051: d=0000h=05m=23s=16 diag=0x3D 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00   no=0052: d=0000h=05m=23s=18 diag=0x3E 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00   no=0053: d=0000h=05m=24s=45 diag=0x1E 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00   no=0054: d=0000h=05m=25s=16 diag=0x1E 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00   no=0055: d=0000h=05m=25s=57 diag=0x1E 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00   no=0056: d=0000h=05m=25s=59 diag=0x3D 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00   no=0057: d=0000h=05m=25s=59 diag=0x3E 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00   no=0058: d=0000h=05m=32s=27 diag=0x2A 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00   no=0059: d=0000h=05m=32s=27 diag=0x1E 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00   no=0060: d=0000h=05m=32s=29 diag=0x3D 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00   no=0061: d=0000h=05m=32s=29 diag=0x14 00 04 02 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00   no=0062: d=0000h=05m=33s=18 diag=0x2A 00 04 02 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00   no=0063: d=0000h=05m=33s=18 diag=0x1E 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00   no=0064: d=0000h=05m=33s=20 diag=0x3D 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00   no=0065: d=0000h=05m=33s=20 diag=0x29 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00   no=0066: d=0000h=05m=33s=20 diag=0x15 03 20 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00

This is a very mean error to find:

The slave always reboots because of an initialization error:

DP Configuration Entry  Error

03 = slot

20 = config byte (master)

00 = config byte (slave)

00 = S7_400_Mode off

Therefore the problem is found:

Module number 3 is faulty.

The master requests a digital out byte 20hex but the slave recognized a unknown module 00hex on the vbus.

no=0067: d=0000h=05m=33s=20 diag=0x1E 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00   no=0068: d=0000h=05m=33s=22 diag=0x3D 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00   no=0069: d=0000h=05m=33s=22 diag=0x29 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00   no=0070: d=0000h=05m=33s=22 diag=0x15 03 20 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00   no=0071: d=0000h=05m=33s=22 diag=0x1E 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00   no=0072: d=0000h=05m=33s=24 diag=0x3D 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00   no=0073: d=0000h=05m=33s=24 diag=0x29 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00   no=0074: d=0000h=05m=33s=24 diag=0x15 03 20 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00   no=0075: d=0000h=05m=33s=24 diag=0x1E 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00   no=0076: d=0000h=05m=33s=26 diag=0x3D 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00   no=0077: d=0000h=05m=33s=26 diag=0x29 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00   no=0078: d=0000h=05m=33s=26 diag=0x15 03 20 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00   no=0079: d=0000h=00m=00s=02 diag=0x3D 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00   no=0080: d=0000h=00m=00s=03 diag=0x3E 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00   no=0081: d=0000h=00m=35s=37 diag=0x3D 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00   no=0082: d=0000h=00m=36s=02 diag=0x3E 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00   no=0083: d=0000h=01m=37s=57 diag=0x2A 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00   no=0084: d=0000h=01m=37s=57 diag=0x1E 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00  ÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿÿ

The internal slave information buffer contains additional binary information. This can only be interpreted by VIPA development people. It is used to find out possible software problems or localize errors that can’t be described with the provided diagnostic messages.

According to diagcnt=0084,

this is the latest message in the ringbuffer.

VIPA hopes that you will never need to work with „Slave info tool“. But in case of errors you are provided with strong diagnostic features to trap the bug. Especially the timestamp feature facilitate the hunt for random events („every wednesday at 12:00pm my sensor data is lost for 10 seconds....“)

Success

VIPA GmbH